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Monthly O&M review - minutes
2026-06-18, 10:00 to 11:30, Quellmoor Ridge O&M building
Chair: Maren Ellingsby (Site Manager). Present: Dario Penwarden, Yusuf Arkwell, Greta Vollan, Tomasz Lebrecht, Callum Rydings. Apologies: Élise Ternaux.
1. Safety
No lost-time injury in May. The actions of near miss INC-2026-003 are closed.
Audit AUD-2026-02: F1 closed on 2026-03-27 (all rescue kits inspected), F2 closed on 2026-03-12, F5 closed on 2026-03-30. F3 is still open: the toolbox talk records are being reconstructed and the due date moves to 2026-07-31. F4 (oil drum bund) is open, due 2026-06-30.
2. Performance in May 2026
Park availability 98.0 % and energy 6,942 MWh. WTG-07 availability 95.2 % because of the gearbox trips.
3. WTG-07 gearbox over-temperature
8D INC-2026-006 was opened on 2026-05-30. WTG-07 has been limited to 2.6 MW since 2026-06-01. Oil analysis TR-OA-2026-0614 arrived on 2026-06-17 with condition ALERT (iron 64 ppm). Callum Rydings will inspect the cooler fan and the radiator; the inspection is planned for 2026-06-24.
4. Blade inspection
Report WBS-2026-031 arrived on 2026-06-03. WTG-04 blade B has a category 4 trailing-edge crack and must be replaced before 2026-09-30 (WO-26-0355). A new blade is ordered from Litware Wind Systems for delivery at the end of August. The crane lift will be planned with Tailspin Heavy Lift for early September. Monthly drone checks continue; the next one is on 2026-07-02.
5. Environment
The bat protection curtailment season started on 1 June for WTG-03, WTG-04 and WTG-05 (permit condition 7.3). Yusuf Arkwell checked the curtailment settings in the turbine controllers on 2026-05-28.
6. Spare parts
There is no HSS bearing FGT-P-22328 in stock since the WTG-10 repair in March. Tomasz Lebrecht will raise a purchase order for two bearings; the supplier lead time is about 10 weeks.
7. Any other business
City Power & Light announced network works on the Skelvane 132 kV circuits in July; the formal curtailment instruction is expected early July.
Actions
	No.
	Action
	Owner
	Due

	1
	Inspect WTG-07 oil cooler fan and radiator
	Callum Rydings
	2026-06-24

	2
	Purchase order for two HSS bearings FGT-P-22328
	Tomasz Lebrecht
	2026-06-22

	3
	Plan the WTG-04 blade lift with Tailspin Heavy Lift
	Dario Penwarden
	2026-07-31

	4
	Close audit finding F3
	Greta Vollan
	2026-07-31

	5
	Bund capacity for oil drums (finding F4)
	Tomasz Lebrecht
	2026-06-30


Next review: 2026-07-16.
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