# SOP-LOTO-001 - Lockout/tagout of wind turbines

Standard operating procedure - Revision C - effective 2024-09-02

| Field | Value |
| --- | --- |
| Document number | SOP-LOTO-001 |
| Revision | C |
| Effective date | 2024-09-02 |
| Owner | Greta Vollan, HSE Coordinator |
| Approved by | Maren Ellingsby, Site Manager |

# 1. Purpose

Protect people working on a turbine against the unexpected release of electrical, hydraulic, mechanical, rotational and thermal energy.

# 2. Scope

All work on WTG-01 to WTG-12 and on the Quellmoor Ridge substation low-voltage boards. High-voltage switching is done only by authorised persons under the switching programme and is outside this procedure.

# 3. Responsibilities

The PTW issuer checks the isolation list before signing the PTW.

Each worker applies a personal padlock and keeps the key.

The O&M Supervisor approves any deviation in writing.

# 4. Energy sources of the LT-32

| Energy | Source | Isolation point |
| --- | --- | --- |
| Electrical 690 V | Generator, converter, auxiliaries | Main circuit breaker in the tower base |
| Electrical 33 kV | Transformer feeder | Ring main unit (authorised persons only) |
| Uninterruptible power | UPS of the controller | UPS output breaker |
| Hydraulic | Pitch and yaw brake accumulators | Relief valves to 0 bar |
| Rotational | Rotor and drivetrain | Rotor lock pins |
| Thermal | Hot gear oil, heaters | Cool-down and heater breaker |

# 5. Personal padlocks and tags

Every worker uses a personal padlock with a name tag. Padlocks without a name tag must not be used. Spare padlocks are issued by the HSE Coordinator.

# 6. Isolation sequence

6.1 Inform the control room and set the turbine to maintenance mode (status S310).

6.2 Stop the turbine from the controller and wait until the rotor speed is below 1 rpm.

6.3 Engage the rotor lock pins; do not engage them above a 10-minute mean wind speed of 15 m/s.

6.4 Open the main circuit breaker and the UPS output breaker; apply padlocks and tags.

6.5 Release the hydraulic pressure of the pitch and yaw brake accumulators to 0 bar.

6.6 Apply the group lock box when more than two people work on the turbine.

# 7. Verification

Try to start the turbine from the local panel, test for absence of voltage at the converter and read 0 bar on the accumulator gauges before work starts.

# 8. Removal

Each worker removes only his or her own padlock. The last person checks that tools are removed and guards are fitted before the turbine leaves maintenance mode.

# 9. Revision history

| Revision | Date | Change |
| --- | --- | --- |
| A | 2019-10-01 | First issue at commercial operation. |
| B | 2021-05-17 | Group lock box added. |
| C | 2024-09-02 | Energy table updated; wind limit for rotor lock pins. |