# SOP-GBX-010 - Gearbox oil change

Standard operating procedure - Revision A - effective 2023-04-03

| Field | Value |
| --- | --- |
| Document number | SOP-GBX-010 |
| Revision | A |
| Effective date | 2023-04-03 |
| Owner | Dario Penwarden, O&M Supervisor |
| Approved by | Maren Ellingsby, Site Manager |
| Applies to | WTG-01 to WTG-12 (Litware LT-32 CCV, Fabrikam FGT-3200 gearbox) |

# 1. Purpose

This procedure describes how to change the gearbox oil of the Quellmoor Ridge turbines safely and without contaminating the new oil.

# 2. Scope

All gearbox oil changes on WTG-01 to WTG-12, whether planned or decided after an oil analysis.

# 3. References

LWS-MM-GBX-32 Rev. D, section 4.3 (Litware maintenance manual, gearbox)

SOP-LOTO-001 Lockout/tagout of wind turbines

SOP-WAH-003 Working at height and rescue

Oil level check at the sight glass

# 4. Safety

A PTW is required. Two technicians minimum; no lone working in the nacelle.

Isolate the turbine according to SOP-LOTO-001 before opening the oil circuit.

Do not start the job if the 10-minute mean wind speed exceeds 15 m/s.

Hot oil: wear chemical gloves, face shield and long sleeves; drain only between 40 and 60 °C.

Keep the spill kit ready at the gearbox and absorbent pads under every connection.

# 5. Materials and tools

Proseware PWG 320 (ISO VG 320): 410 L per turbine, 2 drums PWS-320-D208

Oil filter element FGT-P-11872 (1)

Filter cart with 10 micron element, transfer pump, 3 waste oil containers of 200 L

Torque wrench 20 to 300 Nm, oil sample bottles

# 6. Procedure

6.1 Obtain the PTW, stop the turbine and apply lockout/tagout according to SOP-LOTO-001 (rotor locked, drivetrain isolated).

6.2 Check the oil temperature: drain between 40 and 60 °C. If the oil is colder, run the heaters and the electric oil pump before isolation.

6.3 Take a used-oil sample at the sampling valve for the laboratory.

6.4 Drain the gearbox sump and the cooling and filter circuit into the waste containers (about 410 L).

6.5 Remove the magnetic plug, record the debris and clean the plug.

6.6 Replace the filter element FGT-P-11872 and tighten the filter housing cover screws to 85 Nm.

6.7 Refit the drain plug with a new seal and tighten it to 280 Nm.

6.8 Fill 410 L of Proseware PWG 320 through the filter cart (10 micron).

6.9 Run the electric oil pump for 15 minutes and check all connections for leaks.

6.10 After 20 minutes of standstill check the level at the sight glass and top up if needed.

6.11 Remove the lockout, restart and watch the oil temperature during the first hour. The turbine starts only when the oil sump has reached +10 °C.

6.12 Take a reference oil sample after 24 hours of operation.

6.13 Record the quantities and batch numbers in the work order.

# 7. Waste and records

Waste oil goes to the bunded store in the O&M building and is collected by the licensed carrier. Keep the oil sample results with the work order.

# 8. Revision history

| Revision | Date | Change |
| --- | --- | --- |
| A | 2023-04-03 | First issue (PWG 320). |