# MOC-2025-012 - Gearbox oil grade change to PWG 220

Management of change record - approved 2025-06-18

| Field | Value |
| --- | --- |
| MOC number | MOC-2025-012 |
| Raised | 2025-05-06 by Dario Penwarden, O&M Supervisor |
| Type | Technical change - lubricant |
| Scope | WTG-01 to WTG-12 |
| Reviewed by | Greta Vollan (HSE Coordinator), Yusuf Arkwell (Reliability Engineer) |
| Decision | Approved on 2025-06-18 by Maren Ellingsby, Site Manager |

# 1. Description of the change

Replace Proseware PWG 320 (ISO VG 320) with Proseware PWG 220 (ISO VG 220) in the gearboxes of all 12 turbines, as required by service bulletin SB-LWS-2025-07 Rev. A. Litware support confirmed on 2025-05-20 (ticket LWS-TS-48213) that the bulletin applies to all 12 CCV turbines of Quellmoor Ridge.

# 2. Reason

On 2025-01-21, at -24.6 °C, WTG-02 and WTG-09 needed more than 6 hours of heating before they could start. The bulletin also makes the change a condition of the gearbox warranty.

# 3. Risk assessment

| Hazard | Risk | Control |
| --- | --- | --- |
| Mixing of oils | Residual PWG 320 above 5 % | 60 L flush; label the filler; remove PWG 320 drums from the shelf |
| Cold start | Wrong start parameter | Set GBX_TMIN_START to 5 °C and verify it in the conversion checklist |
| Hot oil and spills | Burns, environmental spill | SOP-GBX-010; spill kit; drain between 40 and 60 °C |
| Availability | About 6 hours downtime per turbine | Plan the campaign in low-wind periods |
| Waste oil | 12 x 470 L of waste oil | Licensed carrier; check the bund capacity |

# 4. Actions

| No. | Action | Owner | Due |
| --- | --- | --- | --- |
| 1 | Revise SOP-GBX-010 to Rev. B | Dario Penwarden | 2025-08-29 |
| 2 | Order 36 drums of PWG 220 and set the minimum stock of PWS-220-D208 to 8 drums | Tomasz Lebrecht | 2025-08-15 |
| 3 | Conversion campaign WTG-01 to WTG-12 | Dario Penwarden | 2025-09-01 to 2025-11-28 |
| 4 | Toolbox talk on cold-weather start-up with the new oil | Dario Penwarden | 2025-11-30 |
| 5 | Update the maintenance plan and the oil sampling schedule | Yusuf Arkwell | 2025-12-15 |
| 6 | Send the Litware completion form within 30 days of each conversion | Dario Penwarden | per conversion |

# 5. Cost

Estimated cost EUR 58,600 (36 drums of PWG 220, 12 filter elements, labour and waste oil disposal), within the 2025 maintenance budget.

# 6. Approval

Approved by Maren Ellingsby, Site Manager, on 2025-06-18. Implementation is reported at the monthly O&M review.