## Tasks
Task ID | Task | System | Interval | Procedure or reference | Duration (h) | Crew | Notes
MP-GBX-01 | Gearbox oil sampling and laboratory analysis | Gearbox | 6 months | LWS-MM-GBX-32 section 4.4 | 1 | 1
MP-GBX-02 | Gearbox oil filter element replacement (FGT-P-11872) | Gearbox | 12 months | SOP-GBX-010 | 1.5 | 2
MP-GBX-03 | Gearbox oil change (PWG 220) | Gearbox | 5 years or on condition | SOP-GBX-010 Rev. B | 6 | 2 | Next planned changes from 2030
MP-GBX-04 | Gearbox endoscope inspection | Gearbox | 24 months | LWS-MM-GBX-32 section 4.4 | 3 | 2
MP-GBX-05 | Gearbox visual inspection and leak check | Gearbox | 6 months | LWS-MM-GBX-32 section 4.4 | 1 | 2
MP-GBX-06 | Vibration trend review (condition monitoring) | Gearbox | monthly | LWS-MM-GBX-32 section 4.4 | 0.5 | 1 | Remote review by the Reliability Engineer
MP-GBX-07 | Oil cooler radiator cleaning and fan current check | Gearbox | 6 months | INC-2026-006 (D7) | 2 | 2 | Added in issue 2 (2026-07-01)
MP-GEN-01 | Generator brush inspection | Generator | 6 months | WI-GEN-014 | 1.5 | 2
MP-GEN-02 | Slip ring cleaning | Generator | 12 months | WI-GEN-014 | 2 | 2
MP-PIT-01 | Pitch bearing bolt re-torque, 100 % of bolts, 1,450 Nm | Pitch | 12 months | SB-LWS-2025-11 Rev. A | 8 | 2
MP-BLD-01 | Blade drone inspection | Rotor | 12 months | Wingtip Blade Services | 1 | 2 | Contractor
MP-YAW-01 | Yaw brake pad inspection | Yaw | 12 months | LT-32 manual chapter 7 | 2 | 2
MP-HYD-01 | Hydraulic accumulator pre-charge check | Hydraulics | 12 months | LT-32 manual chapter 9 | 1.5 | 2
MP-HSE-01 | Rescue kit inspection | Safety | 6 months | SOP-WAH-003 section 7 | 0.5 | 1
MP-HSE-02 | Fall arrest rail and ladder inspection | Safety | 12 months | SOP-WAH-003 | 1 | 2

## Plan 2026
Turbine | Task ID | Planned months | Status at 2026-07-01
WTG-01 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-01 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-01 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-01 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-01 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-01 | MP-GBX-02 | 2026-01 | done
WTG-01 | MP-PIT-01 | 2026-05 | done
WTG-01 | MP-BLD-01 | 2026-05 | done
WTG-01 | MP-GBX-04 | 2027-04 | planned
WTG-02 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-02 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-02 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-02 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-02 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-02 | MP-GBX-02 | 2026-02 | done
WTG-02 | MP-PIT-01 | 2026-05 | done
WTG-02 | MP-BLD-01 | 2026-05 | done
WTG-02 | MP-GBX-04 | 2026-07 | done
WTG-03 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-03 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-03 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-03 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-03 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-03 | MP-GBX-02 | 2026-03 | done
WTG-03 | MP-PIT-01 | 2026-05 | done
WTG-03 | MP-BLD-01 | 2026-05 | done
WTG-03 | MP-GBX-04 | 2027-04 | planned
WTG-04 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-04 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-04 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-04 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-04 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-04 | MP-GBX-02 | 2026-04 | done
WTG-04 | MP-PIT-01 | 2026-05 | done
WTG-04 | MP-BLD-01 | 2026-05 | done
WTG-04 | MP-GBX-04 | 2026-10 | planned
WTG-05 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-05 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-05 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-05 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-05 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-05 | MP-GBX-02 | 2026-05 | done
WTG-05 | MP-PIT-01 | 2026-05 | done
WTG-05 | MP-BLD-01 | 2026-05 | done
WTG-05 | MP-GBX-04 | 2027-04 | planned
WTG-06 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-06 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-06 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-06 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-06 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-06 | MP-GBX-02 | 2026-06 | done
WTG-06 | MP-PIT-01 | 2026-05 | done
WTG-06 | MP-BLD-01 | 2026-05 | done
WTG-06 | MP-GBX-04 | 2026-10 | planned
WTG-07 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-07 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-07 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-07 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-07 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-07 | MP-GBX-02 | 2026-07 | planned
WTG-07 | MP-PIT-01 | 2026-09 | planned
WTG-07 | MP-BLD-01 | 2026-05 | done
WTG-07 | MP-GBX-04 | 2027-04 | planned
WTG-08 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-08 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-08 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-08 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-08 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-08 | MP-GBX-02 | 2026-08 | planned
WTG-08 | MP-PIT-01 | 2026-09 | planned
WTG-08 | MP-BLD-01 | 2026-05 | done
WTG-08 | MP-GBX-04 | 2026-10 | planned
WTG-09 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-09 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-09 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-09 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-09 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-09 | MP-GBX-02 | 2026-09 | planned
WTG-09 | MP-PIT-01 | 2026-09 | planned
WTG-09 | MP-BLD-01 | 2026-05 | done
WTG-09 | MP-GBX-04 | 2027-04 | planned
WTG-10 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-10 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-10 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-10 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-10 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-10 | MP-GBX-02 | 2026-10 | planned
WTG-10 | MP-PIT-01 | 2026-09 | planned
WTG-10 | MP-BLD-01 | 2026-05 | done
WTG-10 | MP-GBX-04 | 2026-10 | planned
WTG-11 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-11 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-11 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-11 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-11 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-11 | MP-GBX-02 | 2026-11 | planned
WTG-11 | MP-PIT-01 | 2026-09 | planned
WTG-11 | MP-BLD-01 | 2026-05 | done
WTG-11 | MP-GBX-04 | 2027-04 | planned
WTG-12 | MP-GBX-01 | 2026-06, 2026-12 | done
WTG-12 | MP-GBX-05 | 2026-03, 2026-09 | done
WTG-12 | MP-GBX-07 | 2026-07, 2027-01 | planned
WTG-12 | MP-GEN-01 | 2026-04, 2026-10 | done
WTG-12 | MP-HSE-01 | 2026-02, 2026-08 | done
WTG-12 | MP-GBX-02 | 2026-12 | planned
WTG-12 | MP-PIT-01 | 2026-09 | planned
WTG-12 | MP-BLD-01 | 2026-05 | done
WTG-12 | MP-GBX-04 | 2026-10 | planned

## Oil sampling
Turbine | Last sample | Report | Oil | Fe (ppm) | PQ index | Condition | Next sample due
WTG-01 | 2026-06-08 | TR-OA-2026-0603 | PWG 220 | 10 | 25 | NORMAL | 2026-12
WTG-02 | 2026-06-08 | TR-OA-2026-0604 | PWG 220 | 27 | 22 | NORMAL | 2026-12
WTG-03 | 2026-06-08 | TR-OA-2026-0605 | PWG 220 | 22 | 25 | NORMAL | 2026-12
WTG-04 | 2026-06-09 | TR-OA-2026-0606 | PWG 220 | 27 | 22 | NORMAL | 2026-12
WTG-05 | 2026-06-09 | TR-OA-2026-0607 | PWG 220 | 13 | 9 | NORMAL | 2026-12
WTG-06 | 2026-06-09 | TR-OA-2026-0608 | PWG 220 | 24 | 12 | NORMAL | 2026-12
WTG-07 | 2026-06-10 | TR-OA-2026-0614 | PWG 220 | 64 | 112 | ALERT | 2026-07-10 (resample within 30 days)
WTG-08 | 2026-06-10 | TR-OA-2026-0610 | PWG 220 | 27 | 17 | NORMAL | 2026-12
WTG-09 | 2026-06-10 | TR-OA-2026-0611 | PWG 220 | 22 | 11 | NORMAL | 2026-12
WTG-10 | 2026-06-11 | TR-OA-2026-0612 | PWG 220 | 14 | 26 | NORMAL | 2026-12
WTG-11 | 2026-06-11 | TR-OA-2026-0613 | PWG 220 | 14 | 12 | NORMAL | 2026-12
WTG-12 | 2026-06-11 | TR-OA-2026-0615 | PWG 220 | 25 | 26 | NORMAL | 2026-12

## Revision log
Issue | Date | Change | Author
1 | 2025-12-15 | Plan 2026 issued; oil sampling schedule updated for PWG 220 (MOC-2025-012 action 5). | Dario Penwarden
2 | 2026-07-01 | Task MP-GBX-07 added for all turbines after INC-2026-006; WTG-02 endoscope brought forward to July. | Dario Penwarden

## About
FICTIONAL - NOT FOR OPERATIONAL USE
Maintenance plan 2026, issue 2 of 2026-07-01, Quellmoor Ridge Wind Farm.
Owner: Dario Penwarden, O&M Supervisor, Contoso Renewables.
Sheets: Tasks (task catalogue), Plan 2026 (per turbine), Oil sampling, Revision log.
FICTIONAL - NOT FOR OPERATIONAL USE